## Slide 1: Configuring IP Cluster I/O Module (CLIM)
Module 9

## Slide 2: Module Objectives
  Specific SCF commands for IP CLIMS
  Settings for Data Provider process
  General command structure climconfig
  Adding and configuring interfaces
    Simple interface
    IP alias
  Configuring for fault-tolerance
    Bonding - types supported - fail-over on interface and link level
    CLIM-to-CLIM - per provider fault tolerance - fail-over on CLIM level
  Adding and configuring routes
    Generic routes
    Specific routes
  Looking at TCP/IP configurations and collecting information
Notes: <footer>
<header>
<date/time>

## Slide 3: IP configuration considerations for IP CLIMs
There are parts that are configured on the NonStop System
  CIP subsystem, including general IP settings.
  files directly accessed by the TCP library bound to the application on the NonStop system. Examples are the HOSTS and RESCONF file in the subvolume $SYSTEM.ZTCPIP.
  Routes that point to a certain CLIM
There are parts that are configured on the CLIMs
  Routes (at CLIM level) and ARP entries are normally configured through the climconfig command and stored on the CLIMs

## Slide 4: IP configuration files
Because the Guardian applications use the old time socket interface bound to their programs object file on the NonStop Systems (since D30), they still use the same TCP/IP configuration files accessed by this library. These files have the same layout and function.
Examples:
    $SYSTEM.ZTCPIP.HOSTS
    $SYSTEM.ZTCPIP.IPNODES (only with the newer IPv6 libraries)
    $SYSTEM.ZTCPIP.RESCONF
    $SYSTEM.ZTCPIP.SERVICES
    $SYSTEM.ZTCPIP.NETWORKS
    $SYSTEM.ZTCPIP.PROTOCOL
Also the defines for these files are the same.

## Slide 5: SCF CIP subsystem

## Slide 6: NonStop CIP Subsystem Object Hierarchy through CIPMAN
PROCESS ($ZZCIP)
(CIP Manager Process)
MON (CIPMON Process)
CLIM (CLIM object)
ROUTE
(The ROUTE Object)
PROVIDER (Transport service Provider)
Notes: <footer>
<header>
<date/time>
  The CIP subsystem two PROCESS object types:
    CIPMAN
    CIPSAM
  The CIPMAN and CIPSAM processes support different subordinate objects and have different SCF command syntax, attribute definitions, and displays.
  The objects are as follows:
    CLIM - Cluster I/O Module object.
    MON - CIP Monitor process object.
    PROCESS (CIPMAN) - CIP Manager $ZZCIP process.
    PROCESS (Provider) - Provider object represents the transport service provider.
    CIPSAM - A Nonstop process pair that provides applications a name for transport-service Provider. CIPSAM supports a limited number of SCF commands for controlling the process itself.
    ROUTE - Each ROUTE object specifies a CLIM to be used for routing the network traffic.

## Slide 7: SCF Command Matrix TCP/IP /PL and TCP/IPv6 (1 of 2)
COMMAND /OBJECT TYPE | CLIM | MON | PROCESS (CIPMAN) | PROCESS (CIPSAM) | PROVIDER | ROUTE
ABORT | X | X | X | X | X | 
ADD | X |  |  |  | X | X
ALTER |  |  |  |  | X | 
DELETE | X |  |  |  | X | X
INFO | X |  | X | X | X | X
LISTOPENS |  | X |  |  | X | 
NAMES | X |  | X |  | X | X
PRIMARY |  |  | X | X |  | 
START | X |  | X |  | X | 
STATS | X | X |  |  |  | 
STATUS | X | X | X |  | X | 
STOP | X | X | X | X | X | 
SWITCH | X |  |  |  |  | 
TRACE | X | X | X | X | X | 
VERSION | X | X | X | X |  | 
NOTE: 1. Object type NULL for VERSION and NAMES.
Notes: <footer>
<header>
<date/time>

## Slide 8: ZZCIP Manager process
  Process should be started as generic process in NonStop Kernel subsystem in SCF at system load:
      ADD PROCESS $ZZKRN.ZZCIP , AUTORESTART 10 , &
      BACKUPCPU 1 , HOMETERM $ZHOME , &
      INFILE $ZHOME , NAME $ZZCIP , &
      OUTFILE $ZHOME , PRIMARYCPU 0 , &
      PRIORITY 146 , STARTUPMSG "<BKUP-CPU>" , &
      PROGRAM $SYSTEM.SYSTEM.CIPMAN , STARTMODE SYSTEM , &
      STOPMODE SYSMSG , &
      TYPE OTHER , USERID SUPER.SUPER
  INDO gives only very brief information. STATUS, DETAIL gives some more useful information:
      SCF> info PROCESS $ZZCIP
      CIP Info PROCESS \BLING.$ZZCIP
      PPID................... ( 0,364) BPID................... NONE
      7-> status process $ZZCIP, detail
      CIP Detailed Status PROCESS $ZZCIP
      Heap Memory Limit........ 1609248768
      Heap Memory Used......... 262144
      PID Primary.............. (0,364)
      PID Backup............... NONE
      Priority................. 200
      QIO Pool Current......... 0
      QIO Pool Limit........... 0
      State.................... STARTED
Notes: SCF commands for the CIP Manager process are: ABORT, INFO, NAMES, PRIMARY, START, STOP, STATUS, TRACE and VERSION

## Slide 9: The MON object - CIP monitor process
  Opposed to NonStop TCP/IPv6 for the CIP subsystem the monitors need to be started as generic processes;
      ADD PROCESS $ZZKRN.CIPMON , &
      AUTORESTART 10 , CPU ALL , &
      DEFAULTVOL $SYSTEM.NOSUBVOL , &
      HIGHPIN ON , HOMETERM $ZHOME , &
      INFILE $ZHOME , NAME $ZCM , &
      OUTFILE $ZHOME , PRIORITY 146 , &
      PROGRAM $SYSTEM.SYSTEM.CIPMON , &
      SAVEABEND OFF , STARTMODE SYSTEM , &
      STOPMODE SYSMSG , TYPE OTHER , &
      USERID SUPER.SUPER
  SCF status mon $ZZCIP.*
        CIP Status MON
        MON Pid Status Priority Trace
        ZCM00 0,368 STARTED 200 OFF
        ZCM01 1,366 STARTED 200 OFF
        ZCM02 2,301 STARTED 200 OFF
        ZCM03 3,309 STARTED 200 OFF
Notes: SCF commands for the MON object: ABORT, LISTOPENS, STOP, STATS, STATUS, TRACE, VERSION

## Slide 10: The MON object - CIP monitor process - continued
  SCF Listopens mon shows you:
    CIP Listopens MON \BLING.$ZZCIP.ZCM00
    Openers Ppid State Proto Lport Provider CLIM
    \BLING.$ZTN0 0,407 ESTAB TCP telnet ZTC0 N1002582
    \BLING.$ZCMOM 0,355 ESTAB TCP 5988 ZTC0 N1002581
    \BLING.$ZTN0 0,407 LISTEN TCP telnet ZTC0 *mult*
    \BLING.$LSN0 0,406 LISTEN TCP 6446 ZTC0 *mult*
    ...
  Listopens, detail gives even a lot more
    CIP Detailed Listopens MON \BLING.$ZZCIP.ZCM00
    Opener:\BLING.$ZTN0 Ppid: 0,407 Bpid: 0, 0
    Plfn:3 Blfn:0
    Proto:TCP State:ESTAB SendQ:29 RecvQ:0
    Provider:ZTC0 CLIM:N1002582 CLIM-FD:52
    Lport:telnet Laddr:16.26.84.48
    FPort:1271 Faddr:16.151.75.180
    ...
    Opener:\BLING.$ZTN0 Ppid: 0,407 Bpid: 0, 0
    Plfn:2 Blfn:0
    Proto:TCP State:LISTEN SendQ:0 RecvQ:0
    Provider:ZTC0 CLIM:*mult* CLIM-FD:38
    Lport:telnet Laddr:0.0.0.0
    FPort:0 Faddr:0.0.0.0

## Slide 11: CLIM object
  Lots of commands here
      ADD CLIM $ZZCIP.N1002582 , &
      MODE IP , &
      CONNPTS 1 , &
      LOCATION (100 , 2 , 5 , 8 , 2 ) , &
      PROVIDER ZTC0
  Info, detail
      CIP Detailed Info CLIM \BLING.$ZZCIP.N1002582
      Mode....................... IP
      Configured Location........ Group 100 , Module 2 , Slot 5 , Port 8 , Fiber 2
      ConnPts.................... 1
      X1 Location................ Group 100 , Module 2 , Slot 5 , Port 8 , Fiber 2
      Y1 Location................ Group 100 , Module 3 , Slot 7 , Port 8 , Fiber 2
      SvNet ID 1................. 0x000E3F21
      Maintenance Interface IP... 192.168.37.82
      Network CLIM Information:
      Provider................... ZTC0
      Index...................... 1
      Maintenance Providers Configured:
      ZTCP1 192.168.36.11
Notes: SCF commands for the CLIM object: ABORT, ADD , DELETE, INFO, NAMES, START, STATS, STATUS, STOP, SWITCH, TRACE, VERSION

## Slide 12: CLIM statistics
  stats clim N1002582
  CIP Stats CLIM \BLING.$ZZCIP.N1002582
  Sample Time ... 10 Nov 2009, 15:18:14.000
  Reset Time .... 30 Oct 2009, 15:10:40.000
  CLIMMON STATS
  Event Log Entries......... 0 Restarts.................. 1
  CLIMAGT Failures.......... 0 CIPSSRV0 Failures......... 0
  CLIMAGT STATS
  Event Log Entries........... 1
  Buffer denials.............. 0
  IT-API errors............... 0
  Last IT-API error code...... 0
  Linux errors................ 267
  Last Linux errno............ 2
  Current bfr bytes in use.... 160
  High bfr bytes in use....... 3328
  Total msgs sent............. 689088
  Total msgs received......... 663685
  Current connected Cpus...... 4 High connected Cpus......... 4
  Queued Commands............. 1 Failed Commands............. 0
Notes: The rest of the CLIM statistics output:
  CIPSSRV0 STATS
  Event Log Entries........... 0
  Buffer denials.............. 0
  IT-API errors............... 0
  Last IT-API error code...... 0
  Linux errors................ 0
  Last Linux errno............ 0
  Current bfr bytes in use.... 11120640
  High bfr bytes in use....... 13225984
  Total msgs sent............. 263882
  Total msgs received......... 266705
  Total bytes sent............ 5224520
  Total bytes received........ 411279
  Current connected Cpus...... 4 High connected Cpus......... 4
  Deferred Sends.............. 0 Failed Commands............. 0
  Current TCP Listen Sockets.. 21 High TCP Listen Sockets..... 21
  Current UDP Sockets......... 2 High UDP Sockets............ 3
  Current TCP Connections..... 6 High TCP Connections........ 6
  SCF -> HELP CIP STATS CLIM
  gives you all the details what the counter mean.
To see the Ethernet, TCP, UDP and other protocol related statistics to judge the line quality or investigate protocol related issues you need the network statistics of the clim.
To get the CLIM network statistics you can use the commands:
TACL> climcmd <clim> ip -s ...
or
TACL> climcmd <clim> netstat -s ...

## Slide 13: STATUS CLIM
    status clim N1002582 ,detail
    CIP Detailed Status CLIM \BLING.$ZZCIP.N1002582
    Mode...................... IP
    CLIM HW Connection Status. Connected
    State..................... STARTED
    ConnPts................... 1
    X1 Location............... Group 100 , Module 2 , Slot 5 , Port 8 , Fiber 2
    Expected Y1 Location...... Group 100 , Module 3 , Slot 7 , Port 8 , Fiber 2
    X1 Connection Status...... Connected
    Y1 Connection Status...... Connected
    Trace Status.............. OFF
    Last Restart Time......... 30 Oct 2009, 15:10:22.000
    CLIM Hostname............. N1002582
    CIP SW Version............ T0853H01_01MAY2009_12MAY2009_AAL
    Network SW Version........ T0691H01_01MAY2009_AAL_CLIM_U11
    Storage SW Version........
    Number of Socket Servers.. 1
    Linux Version:
    Linux 2.6.18-24etch0hpde1.1-clim-amd64 #1 SMP PREEMPT Fri Mar 20 17:32:07 UTC 2
    009
    Fabric Status:
    CIPMON Mgmt Data
    ZCM00 XY-1 XY-1
    ZCM01 XY-1 XY-1
    ZCM02 XY-1 XY-1
    ZCM03 XY-1 XY-1
Notes:     And the rest of the output:
    CLIM Maintenance Interface Status & IP Addresses:
    eth0 Sts:UP Lkp:UP IPv4: 192.168.37.82
    IPv6: fe80::21e:bff:febe:e7e
    Maintenance Provider Interface Status & IP Addresses:
    eth0:0 Sts:UP Lkp:UP IPv4: 192.168.36.11
    Data Interface Status & IP Addresses:
    Flg Name Status LkP Master / IP Family & Address
    eth5 UP UP
    IPv4: 16.26.84.48
    IPv6: fe80::21f:29ff:fe59:f50e
    eth1 UP DOWN
    IPv6: fe80::21e:bff:febe:e7c
    eth4 UP DOWN
    IPv4: 192.168.36.233
    IPv6: fe80::21f:29ff:fe59:f50f
    eth3 UP UP
    IPv4: 192.168.36.231
    IPv6: fe80::21f:29ff:fe59:f50c
    eth2 UP UP
    IPv4: 192.168.36.230
    IPv6: fe80::21f:29ff:fe59:f50d
    lo UP --
    IPv4: 127.0.0.1
    IPv6: ::1
    Interface Failover Configuration and Status:
    Flg Name Failover/(Assoc) Fovr Current Index
    N1002582.eth4 -- N1002582.eth4 0x000000010F
    N1002582.eth1 -- N1002582.eth1 0x000000010E
    N1002582.eth2 -- N1002582.eth2 0x000000010B
    (X) N1002582.eth5 N1002581.eth5 Home N1002582.eth5 0x000000010C
    N1002582.eth3 -- N1002582.eth3 0x000000010D

## Slide 14: Provider Process object
  The CIPSAM process is added as a generic process in the NonStop Kernel subsystem:
        ADD PROCESS $ZZKRN.ZTC0 , &
        AUTORESTART 10 , BACKUPCPU 1 , &
        HIGHPIN ON , HOMETERM $ZHOME , &
        INFILE $ZHOME , NAME $ZTCO , &
        OUTFILE $ZHOME , PRIMARYCPU 0 , &
        PRIORITY 157 , PROGRAM $SYSTEM.SYSTEM.CIPSAM , &
        SAVEABEND OFF , STARTMODE SYSTEM , &
        STARTUPMSG "<BCKP-CPU>" , STOPMODE STANDARD , &
        TYPE OTHER , USERID SUPER.SSUPER
  Then add it as a PROVIDER in the CIP subsystem:
        ADD provider $zzcip.ztc0, type ipdata, &
        hostname “systema”, hostid 19.26.84.47 , &
        family INET
  Finally you can start the PROVIDER in the CIP subsystem:
        START provider $zzcip.ztc0
      the provider will only get into a started state in the associated CLIM is in a started state
Notes: Complete ADD PROVIDER Command Syntax:
ADD PROVIDER $ZZCIP.provider-name
[[,TYPE IPDATA]
[,SHARE-PORTS num-ports]
[,FAMILY {INET|DUAL}]|
,TYPE MAINTENANCE, CLIM clim-name, IPADDRESS ip-addr]
[,TPNAME tp-name]
[,HOSTNAME hostname]
[,HOSTID hostid]
[,BRECVPORT (port [,port [...]])]
[,TCP-LISTEN-QUE-MIN queue-size]
Specific parameters:
SHARE-PORTS num-ports
Is the number of ports reserved for TCP, SCTP, and UDP shared-ephemeral ports that can be on multiple CLIMs. Shared-ephemeral ports are those assigned by the CIP subsystem when an application has not bound to a specific IP address and interface. This attribute is valid only for a PROVIDER of TYPE IPDATA. The default is 1000. Possible values are in the range from 100 to 4000.
BRECVPORT ( [ , port ] [ , port ] ... )
Specifies the UDP ports that receive broadcast messages on sockets bound to specific IP addresses or INADDR_ANY. Ports not in the list can receive broadcast messages only on sockets bound to ADDR_ANY. Up to eight port numbers can be specified. The range for each port number is 1 to 65535. The default is no port specified.
TCP-LISTEN-QUE-MIN queue-size
Is the minimum queue length that is allocated on a TCP socket when a socket LISTEN or
ACCEPT_NW1 function call is handled. This value is used if the queue length specified in
the socket request is lower, otherwise the queue length in the socket request is used. The
default is 128. The range is 1 to 1024.

## Slide 15: Getting info about the CIPSAM PROCESS and PROVIDER object (1 of 2)
  CIPSAM and PROVIDER and TRANSPORT PROVIDER are all the same process, but the names differ in the various contexts.
    In the Kernel subsystem as generic process it is referred to as CIPSAM
    In the CIP subsystem it is referred to as PROVIDER object type
    As TCP^PROCESS^NAME define for TCP/IP socket programs it is referred to as TRANSPORT PROVIDER
  The INFO PROVIDER only gives the details about the parameters shown as can used for the add PROVIDER.
      SCF-> info provider $zzcip.ztc0,detail
      CIP Detailed Info PROVIDER \BLING.$ZZCIP.ZTC0
      *TPName.................... $ZTC0
      Type...................... IPDATA
      *HostID.................... 16.26.84.47
      *Hostname.................. bling-clim1.gbr.hp.com
      *TCP-Listen-Que-Min........ 128
      *BRecvPort................. No Ports Specified
      *Family.................... INET
      *Share-Ports............... 1000
      Associated CLIMs:
      Name Index
      N1002581 0
      N1002582 1

## Slide 16: Getting info about the CIPSAM PROCESS and PROVIDER object (2 of 2)
  The INFO PROCESS of the CIPSAM process is only giving you dummy information apart from the program name and the trace information.
      SCF-> info process $ztc0,detail
      TCPIP Detailed Info PROCESS \BLING.$ZTC0
      *TCP Send Space......... 0 *TCP Receive Space...... 0
      *UDP Send Space......... 0 *UDP Receive Space...... 0
      *Delay Ack Time......... 0 *Delay Ack.............. OFF
      *Keep Alive Idle........ 0 *Keep Alive Retry Cnt... 0
      *Keep Alive Interval.... 0 QIO Limit.............. 0%
      *Host ID ............... 0.0.0.0
      *Host Name ............. See "SCF->HELP CIP info process" to view values.
      Program Filename ...... \BLING.$SYSTEM.SYS05.CIPSAM
    ...
      Trace Status........... OFF
      Trace Filename ........
    ...
      *TCP Listen Queue Min... 0
      *Initial TTL............ 0
  In fact it points you to the SCF HELP CIP INFO PROCESS help information which points you to the equivalent CLIMCMD or other commands to get these parameter values.
Notes: The part of the help text that points you to the CLIMCMD or other commands to get the parameter values:
The other attributes are no longer viewable with the CIP info process command.
To view the settings for the other attributes see the descriptions below.
Refer to the CIP configuration and Management Manual -
Section 5: IP CIP Migration and Compatibility
Where:
TCP Send Space
tacl> climcmd <clim-name> sysctl net.ipv4.tcp_wmem
TCP Send Space is the space reserved for send operations for the TCP
protocol.
...
QIO Limit
scf->STATUS MON $ZZCIP.ZCMnn, detail
QIO Limit is a percentage between 0 and 100, representing the amount
of queued I/O or shared memory allowed to this process.
Host Id
scf-> INFO Provider $ZZCIP.<provider-name>, DETAIL
Host Id is the ID (usually the host number part of the Internet address
that is assigned to this host). It is a 32-bit number.
...
TCP-MIN-REXMIT-TIMEOUT
This attribute is not supported in the CIP environment.
TCP-MIN-REXMIT-TIMEOUT is the minimum value allowed for the TCP
retransmission timeout. If this value is too low, the TCP/IP process may
generate premature retransmissions. If this value is set too high, real
retransmissions are delayed, increasing the time for error recovery. The
default is 400 milliseconds. The range is 500 to 30000 milliseconds.
...
INITIAL-TTL
tacl> climcmd <clim-name> sysctl net.ipv4.ip_default_ttl
INITIAL-TTL specifies the initial value for UDP and TCP TTL.

## Slide 17: STATUS PROVIDER
Important information about the status of the provider and resources under this provider can be shown using the SCF STATUS PROVIDER command.
  The standard (default) output shows only the process state as TPStatus and the logical state in SCF.
  The DETAIL option gives all the statuses of each interface on each CLIM that is linked to this PROVIDER and the failover status for each interface, even if the interface was not configured for failover.
  The ROUTE option shows the route information at CIP level per provider. (See later for an example and explanation.)
  The syntax for the STATUS PROVIDER command is:
        STATUS PROVIDER $ZZCIP.<provider-name>
        [, { DETAIL | ROUTE [, CPU <cpu> ] } ]
Notes: An example of the STATUS PROVIDER, DETAIL command:
SCF-> status provider $zzcip.ztc0,detail
CIP Detailed Status PROVIDER \BLING.$ZZCIP.ZTC0
State.................... STARTED
TPStatus................. Started
Type..................... IPDATA
Family................... INET
Current Access........... ( 0, 1, 2, 3 )
Trace Status............. OFF
Interface Status & IP Addresses:
Name Current Status LkP Fovr Index
lo UP -- -- 0x0000000001
IPv4: 127.0.0.1
IPv6: ::1
C1002581.eth5 C1002582.eth5 UP UP BkFO 0x0000000007
IPv4: 10.5.8.1
IPv4: 16.26.84.47
IPv6: fe80::21f:29ff:fe5a:a3a
C1002581.bond0 C1002581.bond0 -- -- Home 0x0000000000
IPv4: 0.0.0.0
...
C1002582.eth5 C1002582.eth5 UP UP Home 0x000000010C
IPv4: 16.26.84.48
IPv6: fe80::21f:29ff:fe59:f50e
C1002582.eth3 C1002582.eth3 UP UP -- 0x000000010D
IPv4: 192.168.36.231
IPv6: fe80::21f:29ff:fe59:f50c
C1002582.eth1 C1002582.eth1 UP DOWN -- 0x000000010E
IPv6: fe80::21e:bff:febe:e7c
C1002582.eth4 C1002582.eth4 UP DOWN -- 0x000000010F
IPv4: 192.168.36.233
IPv6: fe80::21f:29ff:fe59:f50f
Interfaces Failover Configuration and Status:
F Home Sts LkP Failover/(Assoc) Sts LkP Current Fovr
C1002581.eth5 -- -- -- -- C1002582.eth5 BkFO
X C1002581.bond0 -- -- -- -- C1002581.bond0 Home
...
C1002582.eth5 UP UP C1002581.eth5 -- -- C1002582.eth5 Home
C1002582.eth3 UP UP -- -- C1002582.eth3 --
C1002582.eth1 UP DOWN -- -- C1002582.eth1 --
C1002582.eth4 UP DOWN -- -- C1002582.eth4 --

## Slide 18: CIP Route objects
  There are two layers of routing now, the CIP level where the ROUTE object points to a certain CLIM for default routing and the CLIM level where the route points to a gateway or a network or a specific host.
  Normally the CIP subsystem ROUTE object is absent and normally not necessary.
  The SCF ADD ROUTE command creates a new ROUTE object in this system associated with an existing IPDATA PROVIDER. By adding a ROUTE, you can cause a PROVIDER to use a specific CLIM for default routing (when there is a valid default route configured on that CLIM). The SCF ROUTE object creates a route from the host to the specified CLIM.
  The syntax:
        ADD ROUTE $ZZCIP.provider-name.route-name
        , CLIM clim-name
        , FAMILY{INET|INET6|DUAL}
        [,PRIORITY priority]
Notes: Note: Do not confuse this ROUTE object with the route information you can get at PROVIDER level with the SCF STATUS PROVIDER $ZZCIP.<provider name>, ROUTE.
Those routes are automatically generated mainly from the route information at CLIM level.

## Slide 19: SCF CIPSAM process

## Slide 20: NonStop CIPSAM object hierarchy
PROCESS (e.g. $ZTC0)
(CIPSAM - Socket Access Method)
SUBNET
Notes: <footer>
<header>
<date/time>
  The SCF interface directly to the CIPSAM object has been provided for historical reasons.
  It only offers a very rudimentary interface and very limited functionality.
  It has only two object types, PROCESS and SUBNET.
  Where the object type PROCESS is the CIPSAM process, e.g $ZTC0.
  The object type name SUBNET is maintained for compatibility, it really refers to a home CLIM interface as seen from the host. SUBNET object names are generated by CIPSAM and consist of "#SN" followed by a four-digit number.
  The PROCESS object is already shown a few slide ago.

## Slide 21: SCF SUBNET object
  Again, this object is only for compatibility reasons and you can only do STATUS and INFO commands.
  Examples:
  SCF-> status subnet $ZTC0.*
  TCPIP Status SUBNET $ZTC0.*
  Name Status
  #SN010f STARTED
  #SN0001 STARTED
  ...
  SCF-> info subnet $ZTC0.*
  TCPIP Info SUBNET $ZTC0.*
  Name Devicename *IPADDRESS TYPE *SUBNETMASK SuName QIO *R
  #SN010f N1002582.eth4 192.168.36.233 ETHERNET %HFFFF0000 ON N
  ...
  SCF-> info subnet $ZTC0.*
  TCPIP Detailed Info SUBNET \BLING.$ZTC0.*
  Name Devicename *IPADDRESS TYPE *SUBNETMASK SuName QIO *R
  #SN010f N1002582.eth4 192.168.36.233 ETHERNET %HFFFF0000 ON N
  Trace Status ........ OFF
  Trace Filename ......
  Interface MTU ....... 1500
  Gateway ............. OFF

## Slide 22: climconfig

## Slide 23: CLIMCONFIG
  The CLIM command climconfig(1) is recommended to be used rather than the direct Linux commands. The reason is that the climconfig command not only applies the configuration changes but also stores the settings in files. This makes it possible to reload them after the CLIM has been restarted and makes it possible to make backups of these settings with the climbkup command.
  The syntax:
  Usage: climconfig OBJECT {[OPTIONS] | -help}
  climconfig -help
  where OBJECT := { psk | sp | sa | remote | vpn |
  interface | slaveinterface |
  tunnel | ip | route | snmp |
  arp | bondmode | failover |
  hostname | sysctl }
Notes: For details about the climconfig command arguments, see the following man pages:
CLIMCMD {clim-name|ip-address} man climconfig.arp
CLIMCMD {clim-name|ip-address} man climconfig.bondmode
CLIMCMD {clim-name|ip-address} man climconfig.failover
CLIMCMD {clim-name|ip-address} man climconfig.hostname
CLIMCMD {clim-name|ip-address} man climconfig.interface
CLIMCMD {clim-name|ip-address} man climconfig.ip
CLIMCMD {clim-name|ip-address} man climconfig.psk
CLIMCMD {clim-name|ip-address} man climconfig.remote
CLIMCMD {clim-name|ip-address} man climconfig.route
CLIMCMD {clim-name|ip-address} man climconfig.sa
CLIMCMD {clim-name|ip-address} man climconfig.slaveinterface
CLIMCMD {clim-name|ip-address} man climconfig.snmp
CLIMCMD {clim-name|ip-address} man climconfig.sp
CLIMCMD {clim-name|ip-address} man climconfig.sysctl
CLIMCMD {clim-name|ip-address} man climconfig.tunnel
CLIMCMD {clim-name|ip-address} man climconfig.vpn
The most important ones or the ones with special considerations are discussed in the rest of this chapter at different places.

## Slide 24: Further climconfig commands (not discussed elsewhere)
  climconfig arp - setting or getting ARP info
  climconfig hostname - setting or getting Hostname of CLIM
  climconfig psk - setting or getting Pre Shared Keys
  climconfig remote - setting or getting Remote configuration for authentication method of pre-shared key
  climconfig sa - setting or getting security associations
  climconfig snmp - setting or getting SNMP configuration settings
  climconfig sp - setting or getting security policies settings
  climconfig tunnel - setting or getting IPv6 over IPv4 tunnels
  climconfig vpn - obtain information about virtual private networks

## Slide 25: Changing CLIM TCP/IP settings with climconfig sysctl
  To change kernel parameters for TCP/IP on a CLIM there is the command:
    TACL> climcmd <clim name> climconfig sysctl
  The way it works:
    Get a complete list of the configured kernel parameters and their current values.
    TACL> climcmd <clim name> sysctl -a
    Get a list of kernel parameters ever configured with climconfig (default none)
    TACL> climcmd <clim name> climconfig sysctl -info all
    From the output of the sysctl -a select the parameter you like to change and determine the required value. Then issue the command:
    TACL> climcmd <clim name> climconfig sysctl -update <parameter> <value>
    Or when the parameter has multiple values:
    TACL> climcmd <clim name> climconfig sysctl -update <parameter> ’<value> ... <value>’
    EXAMPLES:
    TACL> CLIMCMD n100253 climconfig sysctl -update net.ipv4.conf.all.forwarding 1
    TACL> CLIMCMD n100253 climconfig sysctl -update net.ipv4.tcp_rmem ’4096 87380 1048576’
    IMPORTANT NOTE: ALL CLIMS IN ONE PROVIDER NEED TO BE STOPPED TO CHANGE ANY PARAMETER AND ALL CLIMS SHOULD HAVE THE SAME PARAMETER VALUES WITHIN A PROVIDER.
Notes: The reason for this procedure is that the climconfig sysctl command stores its changed values in a file /etc/clim/kernelparam.conf and that file contains only those changed values.
Only these updated values are shown with:
TACL> climcmd <clim name> climconfig sysctl -info all
Or selectively with:
TACL> climcmd n100253 climconfig sysctl -info net.ipv4.tcp_rmem
After changing two parameters the /etc/clim/kernelparam.conf contains:
# VERSIONFILE :01.00
net.ipv4.tcp_keepalive_time | 75
net.ipv4.tcp_rmem | 4096 87380 1048576
The output of the command climconfig sysctl -info all:
TACL> climcmd n1002581 climconfig sysctl -info all
comForte SSH client version T9999H06_20Mar2009_comForte_SSH_0085
net.ipv4.tcp_keepalive_time = 75
net.ipv4.tcp_rmem = 4096 87380 1048576
Termination Info: 0

## Slide 26: Configuring Interface

## Slide 27: Configuring a simple interface and alias IP address
  To configure simple interface:
    Verify that the interface is not already in use
TACL> climcmd <CLIM NAME> climconfig interface -info all
    Add the new interface
TACL> climcmd <CLIM NAME> climconfig interface -add eth2
    Configure the IP parameters for this interface
TACL> climcmd <CLIM NAME> climconfig ip –add eth2 –ipaddress 10.25.100.31 –netmask 255.0.0.0
  To configure an IP alias (a second or yet another IP address for the same interface)
    Add just another IP address the same way:
TACL> climcmd N1002582 climconfig ip –add eth2 –ipaddress 10.25.100.32 –netmask 255.0.0.0

## Slide 28: Configuring Failover

## Slide 29: Configuring Failover
  Two Modes of Failover
    Intra-CLIM
      Failover between two or more interface in the SAME CLIM
        Bonding
    CLIM-to-CLIM failover
      Failover between two interface in DIFFERENT CLIMs
        Failover Pair
Notes: Intra CLIM

## Slide 30: IP CLIM Failover
  Bonding
    Configured with “climconfig (slave) interface”
    leverages Linux Bonding mode
      Bonds two or more physical interfaces into one logical interface
    Seamless failover when link pulse is lost
    Bonding Modes – applies to all bonded interfaces
      1 – Active/Backup
        MAC Address remains constant
      5 – Balanced-TLB (Adaptive Transmit Load Balancing)
        MAC Address remains constant
      6 – Balanced-ALB (Adaptive Load Balancing)
        IPv4 only
        Use ARP to balance receive traffic to multiple MAC addresses
    Very similar to SHAREDIP option in NonStop TCP/IPv6, only now on one CLIM.
Notes: Bonded interfaces share interface resources among multiple physical interfaces. They can be configured to be similar to NonStop TCP/IPv6 failover with the SHAREDIP option except that the interfaces must be in the same CLIM and are not limited to just two interfaces. Bonded interfaces do not support a mode similar to the NonStop TCP/IPv6 NONSHAREDIP option in which each interface has a different IP address until failover.
You can have however two IP addresses configured on one bond, but both IP addresses are serviced on each interface the same. Traffic is not separated as in a NONSHAREDIP configuration in a normal state.

## Slide 31: Bonding
CLIM
3
1
2
4
5
bond0
Provider ZTC0
IPA: 10.2.100.11

## Slide 32: Configuring Bonding
  Verify and maybe set the bonding mode
  TACL> climcmd n1002582 climconfig bondmode -info
  comForte SSH client version T9999H06_20Mar2009_comForte_SSH_0085
  Bonding Mode : 1 ( active-backup )
  Termination Info: 0
  TACL> climcmd N1002582 climconfig bondmode –modify 6
  comForte SSH client version T9999H06_20Mar2009_comForte_SSH_0085
  Bonding Mode successfully changed
  Termination Info: 0

## Slide 33: Create Bond and add interfaces to Bond
  Create bond
        TACL> climcmd n1002581 climconfig interface –add bond0
  Add first interface
        TACL> climcmd n1002581 climconfig slaveinterface -configure bond0 –add eth3
  Add second interface
        TACL> climcmd n1002581 climconfig slaveinterface -configure bond0 –add eth4
  Configure one or more (aliases) IP address on Bond
        TACL> climcmd n1002581 climconfig ip –add bond0 -ipaddress 10.2.100.11 –netmask 255.255.0.0

## Slide 34: IP CLIM Failover
  CLIM-to-CLIM failover
    Configured with “climconfig failover”
    Manage by NonStop Host (CIPMAN)
    Occurs when an interface (all slaves of a bond) or CLIM fails
    Interface Resources (IP Address, Routes) moved from failed interface to failover interface on the failover CLIM
    TCP and SCTP connections are lost and reset. Similar to losing the CPU hosting the TCP/IP process on Conventional TCP/IP
      Clients must reconnect
    UDP and TCP Listening sockets are migrated to the new CLIM
      Servers continue uninterrupted

## Slide 35: IP CLIM Failover (Cont)
  CLIM-to-CLIM failover
    Requires operator intervention to restore the interface to its home CLIM (SCF SWITCH)
    Routing considerations
      default routes
      multiple routes to destination with differing gateways
  Both CLIMs need to be configure under the same PROVIDER object in SCF.
  Very similar to NONSHAREDIP option in NonStop TCP/IPv6
  The failover interface must be in the same broadcast domain as the home interface. In other words both addresses must be in the same IP subnet.

## Slide 36: Failover Pair
CLIM
3
1
2
4
5
CLIM
3
1
2
4
5
ETH5
ETH5
Failover Pair
Provider ZTC0
IPA: 10.2.100.11
IPA: 10.2.100.12

## Slide 37: Failover Pair
CLIM
3
1
2
4
5
CLIM
3
1
2
4
5
bond0
ETH5
Failover Pair
Provider ZTC0
IPA: 10.2.100.11
IPA: 10.2.100.12

## Slide 38: Failover Pair – Maximum Fault Tolerance
CLIM
3
1
2
4
5
CLIM
3
1
2
4
5
bond0
bond0
Failover Pair
Provider ZTC0
IPA: 10.2.100.11
IPA: 10.2.100.12

## Slide 39: Create IP CLIM failover environment
  Decide to use bonds or simple interfaces on each clim
  In the example we use two bonds, like the one we already created on one CLIM. We assume here that both bonds are created with two IP addresses in the same broadcast domain.
  Now configure the failover on one CLIM
    TACL> climcmd n1002581 climconfig failover –add bond0 -dest n1002582.bond0
    comForte SSH client version T9999H06_20Mar2009_comForte_SSH_0085
    Added the Failover Configuration.
    Termination Info: 0
  And configure the failover on the other CLIM
    TACL> climcmd n1002582 climconfig failover –add bond0 -dest n1002581.bond0
    comForte SSH client version T9999H06_20Mar2009_comForte_SSH_0085
    Added the Failover Configuration.
    Termination Info: 0
  Verify the failover configuration
    TACL> climcmd n1002581 climconfig failover –info n1002581 -interface bond0
    comForte SSH client version T9999H06_20Mar2009_comForte_SSH_0085
    SOURCE DESTINATION
    n1002581.bond0 n1002582.bond0
    Termination Info: 0

## Slide 40: Verify CLIM-to-CLIM Failover
  The SCF STATUS PROVIDER, DETAIL shows the failover configuration and status.
SCF-> STATUS PROVIDER $ZZCIP.ZTC0
...
Interfaces Failover Configuration and Status:
F Home Sts LkP Failover/(Assoc) Sts LkP Current Fovr
N1002581.eth5 UP UP N1002582.eth5 UP UP N1002582.eth5 Home
N1002581.bond0 -- -- -- -- N1002581.bond0 --
N1002581.bond1 -- -- -- -- N1002581.bond1 --
N1002582.eth2 UP UP -- -- N1002582.eth2 --
N1002582.eth5 UP UP N1002581.eth5 -- -- N1002582.eth5 Home
N1002582.eth3 UP UP -- -- N1002582.eth3 --
N1002582.eth1 UP DOWN -- -- N1002582.eth1 --
N1002582.eth4 UP DOWN -- -- N1002582.eth4 --
      The Home column lists all interfaces within the provider
      The Failover column shows the configured failover interface
      The Current column shows which interface currently owns the resources (of the interface under Home column)
      The example below shows the output when there are no failures in network

## Slide 41: Switch CLIM
  The SWITCH CLIM command initiates a manual CLIM-to-CLIM failover operation. It can specify either a single interface or all the interfaces on a CLIM.
  Syntax:
        SCF-> SWITCH CLIM $ZZCIP.clim-name
        {,FAILOVER | ,RESTORE }[,INTF intf-name]
        [,FORCED]
      clim-name Is the name of the CLIM containing the interface(s) upon which to perform failover. Wildcard characters are not allowed.
      FAILOVER Moves all resources off the specified interface(s) to the alternate failover location(s).
      RESTORE Moves the home resources of the specified interface(s) back to the home interface(s).
      INTF intf-name Specifies the name of a single interface for the failover operation. The CLIM name part of the interface name must not be specified. Wildcard characters are not allowed. If this option is omitted, then all interfaces on the CLIM are specified.
      FORCED Indicates that no warning should be issued and confirmation is assumed.
      Example: SCF-> SWITCH CLIM $ZZCIP.N1002532,FAILOVER Open connections still exist, okay to continue? Y

## Slide 42: Adding Routes

## Slide 43: Adding Routes
  Adding, modifying and deleting routes is done at the CLIM level with the climconfig route command.
  The syntax:
  Command to add IPv4 route (non-default):
        CLIMCMD {clim-name|ip-address} climconfig route -add {eth0|eth0:0|interface} -target ipv4-address {-host|-net} [-netmask netmask]
        [-gateway gateway] [-mt metric] [-minrto time]
  Command to add a default IPv4 route:
        CLIMCMD {clim-name|ip-address} climconfig route -add {eth0|eth0:0|interface} -default -gateway gateway [-mt metric] [-minrto time]
  Example:
        TACL> CLIMCMD n100253 climconfig route -add eth2 -default -gateway 10.34.35.1
Notes: Command to delete IPv4/IPv6 routes:
CLIMCMD {clim-name|ip-address} climconfig route -delete {eth0 | eth0:0 |interface} {-host|-net} [-target ip-address] [-netmask netmask] [-gateway gateway][-default] [-force]
Command to delete default IPv4/IPv6 routes:
CLIMCMD {clim-name|ip-address} climconfig route -delete { eth0|eth0:0
|interface} -default -gateway gateway
Command to obtain info about a route:
CLIMCMD {clim-name|ip-address} climconfig route -info [-usrconfig]
Note: The above commands show only the variants for IPv4 routes. Please read the man page climconfig.route for additional variants of these commands for the IPv6 version.

## Slide 44: CIP Routing and Route object
  CLIM with the Longest Prefix Match (LPM) route to the destination is selected
  If there are multiple equal matches, round-robin algorithm is used to pick the route (and thus CLIM)
  Route object priority is used only to select between available ‘default’ routes (not host or net routes)
  Routing on the CLIM uses only destination IP address for picking a route and the LPM on the CLIM is used to select the route
Notes: <footer>
<header>
<date/time>
CIP Routing:
  the Longest Prefix Match (LPM) is used to pick the route to the destination
  if there are multiple CLIMs in the Provider, the CLIM with the LPM route is selected
  if there are multiple CLIMs with the same LPM, then the round-robin is used to pick the route
  if there are two routes with the same LPM on CLIM-A and one route on CLIM-B, then CLIM-A is picked twice as often as CLIM-B
  after the CLIM is selected for routing, the routing logic on the selected CLIM (Linux) is used for picking the route
CLIM Routing:
  the routing by the CLIM also uses the LPM for picking the route
  if there are multiple LPM routes, the first activated one is picked (from the different interfaces)
  use ‘ip route show’ to list the activated routes on a CLIM
  no round-robin is used for picking the route from routes with same LPM
Route object:
  if there is no specific route to a destination, the default route on the CLIM is used
  if there are multiple CLIMs with default routes in a Provider, round-robin algorithm is used to select the CLIM
  if a route object is configured with a higher priority CLIM, the route on that CLIM (and thus the CLIM as well) will be used to route thru the default route, round-robin will not be used to route thru the default route
  the route object priority does not affect any non-default routing (host or net)

## Slide 45: Source Address Selection
  Requested by application
    connected socket
    bind to an address
  Use src hint from the route chosen
    implicitly used
  First IP address of the interface selected for routing
    in the same network as the next hop route
Notes: <footer>
<header>
<date/time>
Source address is selected using the algorithm below -in that order.
Application:
  if the socket is already connected, the source address is already selected
  if the application binds to an IP address, that would be used for the source address in the outgoing packet
From route hint:
  if the route has a ‘src’ hint, then that IP address would be used for source address
  the kernel added routes (routes added when an IP address is added) will always have a src hint
  user added routes do not have an option to specify the src hint
From the interface:
  one of the configured IP addresses on the interface with the selected route will be used as source address
  if there is an IP address in the same IP subnet as the next hop in the route, that would be used
  if there are multiple IP addresses in the next-hop IP subnet, the primary IP address is used (the first in the IP subnet)
  the first activated IP address on the interface will be used
  the first activated IP address is the first one that is listed in the /etc/network/interfaces file
  the IP addresses are activated in the order listed under the interface in the /etc/network/interfaces file
  the home interfaces are activated first before activating the visiting interfaces (in the case of failover)
  the interfaces (within the home/visiting set) are activated in parallel, and the order they are completed is not deterministic

## Slide 46: Verify ROUTE information
Remember there are two layers where routing information is stored and used.
  At the CIP level (the NonStop level). There is a routing table in each CPU for each PROVIDER where routes points to a CLIM. When there is only one CLIM per provider these routes all point to the same CLIM. When there are multiple CLIMs per PROVIDER, these routes point to an appropriate CLIM.
    To see this routing table you can use the following command:
        SCF-> STATUS PROVIDER $ZZCIP.<provider-name> , ROUTE [, CPU <cpu> ]
  At the CLIM level (Linux level). There is only one routing table per CLIM where the routes point to the interface or bond to be used plus a possible gateway to get to the final destination.
    To see this routing table you can use one of the following commands:
        TACL-> CLIMCMD n1002582 climconfig route -info
        (default IPv4 and IPv6)
        or
        TACL-> CLIMCMD n1002582 route [-A inet6]
        (default IPv4 only)
Notes: Examples of the commands:
SCF -> status provider $zzcip.ztc0, route, cpu 0
CIP Detailed Status PROVIDER \BLING.$ZZCIP.ZTC0
Provider State.................. STARTED
Provider Routing Status (CPU 0 ) :
Destination/Prefix Length Type CLIM ROUTE Pri
IPv4: 0.0.0.0/32 H N1002582
IPv4: 127.0.0.1/32 H N1002582
IPv4: 192.168.36.230/32 H N1002582
...
IPv4: 16.26.84.0/24 N1002582
IPv4: 0.0.0.0/0 GS N1002582
...
IPv4: 10.5.8.1/32 H N1002582
IPv4: 192.168.36.233/32 H N1002582
IPv4: 16.26.84.47/32 H N1002582
IPv6: ::/128 H N1002582
...
IPv6: fe80::21f:29ff:fe5a:a3a/128 H N1002582
TACL> CLIMCMD c1002582 climconfig route -info
comForte SSH client version T9999H06_20Mar2009_comForte_SSH_0085
...
Interface : eth5
Destination : 0.0.0.0
Netmask : 0.0.0.0
Gateway : 16.26.84.1
Flags : UG
Metric : 0
Ref : 0
Use : 0
Minimum RTO : Unspecified
...
Termination Info: 0

## Slide 47: Application Configuration

## Slide 48: Application Configuration
  Start the application
    param ztnt^transport^process^name $ztc0
    telserv /cpu 0, name $ztn0, nowait, out $zhome, term $zhome/

## Slide 49: Configuration Verification

## Slide 50: Configuration Verification
  Check the CIP configuration
  Check the network configuration
  Check the failover configuration
  Check the IPsec configuration
  Check the network accessibility
  Check the application
  Test the configuration

## Slide 51: Verify CIP: Provider
SCF-> info provider zzcip.ztc0,detail
CIP Detailed Info PROVIDER \BLING.$ZZCIP.ZTC0
*TPName.................... $ZTC0
Type...................... IPDATA
*HostID.................... 16.26.84.47
*Hostname.................. bling.gbr.hp.com
*TCP-Listen-Que-Min........ 128
*BRecvPort................. No Ports Specified
*Family.................... INET
*Share-Ports............... 1000
Associated CLIMs:
Name Index
N1002581 0
N1002582 1
SCF-> status provider $zzcip.ztc0
CIP Status PROVIDER
Name Status TPStatus Trace
ZTC0 STARTED Started OFF

## Slide 52: Verify CIP: CLIM
SCF-> INFO CLIM $ZZCIP.*
CIP Info CLIM
Name Mode Location ConnPts Provider
S1002531 STORAGE (100 ,2 ,5 ,3 ,1 ) 2 --
S1002533 STORAGE (100 ,2 ,5 ,3 ,3 ) 2 --
S1002541 STORAGE (100 ,2 ,5 ,4 ,1 ) 2 --
S1002543 STORAGE (100 ,2 ,5 ,4 ,3 ) 2 --
N1002581 IP (100 ,2 ,5 ,8 ,1 ) 1 ZTC0
N1002582 IP (100 ,2 ,5 ,8 ,2 ) 1 ZTC0
SCF-> STATUS CLIM $ZZCIP.*
CIP Status CLIM
Name Present State Trace
S1002531 Yes STARTED OFF
S1002533 Yes STARTED OFF
S1002541 Yes STARTED OFF
S1002543 Yes STARTED OFF
N1002581 Yes STARTED OFF
N1002582 Yes STARTED OFF

## Slide 53: Verify Network: CLIM (N1002582)
SCF-> status clim $zzcip.N1002582, detail
...
CLIM Maintenance Interface Status & IP Addresses:
eth0 Sts:UP Lkp:UP IPv4: 192.168.37.82
IPv6: fe80::21e:bff:febe:e7e
Maintenance Provider Interface Status & IP Addresses:
eth0:0 Sts:UP Lkp:UP IPv4: 192.168.36.11
Data Interface Status & IP Addresses:
Flg Name Status LkP Master / IP Family & Address
eth5 UP UP
(V) IPv4: 16.26.84.48
IPv4: 16.26.84.47
(V) IPv6: fe80::21f:29ff:fe5a:a3a
IPv6: fe80::21f:29ff:fe59:f50e
eth1 UP DOWN
IPv6: fe80::21e:bff:febe:e7c
eth4 UP DOWN
IPv4: 192.168.36.232
IPv6: fe80::21f:29ff:fe59:f50f
eth3 UP UP
IPv4: 192.168.36.231
IPv6: fe80::21f:29ff:fe59:f50c
eth2 UP UP
IPv4: 192.168.36.230
IPv6: fe80::21f:29ff:fe59:f50d
lo UP --
IPv4: 127.0.0.1
IPv6: ::1
...

## Slide 54: Verify Network: CLIM (N1002581)
SCF-> status clim $zzcip.N1002581, detail
...
CLIM Maintenance Interface Status & IP Addresses:
eth0 Sts:UP Lkp:UP IPv4: 192.168.37.82
IPv6: fe80::21e:bff:febe:03c
Maintenance Provider Interface Status & IP Addresses:
eth0:0 Sts:UP Lkp:UP IPv4: 192.168.36.11
Data Interface Status & IP Addresses:
Flg Name Status LkP Master / IP Family & Address
eth5 UP UP
(V) IPv4: 16.26.84.47
IPv4: 16.26.84.48
(V) IPv6: fe80::21f:29ff:fe5a:a3a
IPv6: fe80::21f:29ff:fe59:3331
eth1 UP DOWN
IPv6: fe80::21e:bff:febe:893
eth4 UP UP
IPv4: 192.168.36.235
IPv6: fe80::21f:29ff:fe59:3333
eth3 UP UP
IPv4: 192.168.36.234
IPv6: fe80::21f:29ff:fe59:3334
eth2 UP UP
IPv4: 192.168.36.233
IPv6: fe80::21f:29ff:fe59:3335
lo UP --
IPv4: 127.0.0.1
IPv6: ::1
...

## Slide 55: Verify Network: Provider
SCF-> status provider $zzcip.ztc0, detail
...
Interface Status & IP Addresses:
Name Current Status LkP Fovr Index
lo UP -- -- 0x0000000001
IPv4: 127.0.0.1
IPv6: ::1
C1002581.eth5 C1002582.eth5 UP UP BkFO 0x0000000007
IPv4: 10.5.8.1
IPv4: 16.26.84.47
IPv6: fe80::21f:29ff:fe5a:a3a
C1002581.bond0 C1002581.bond0 -- -- Home 0x0000000000
IPv4: 0.0.0.0
...
C1002582.eth5 C1002582.eth5 UP UP Home 0x000000010C
IPv4: 16.26.84.48
IPv6: fe80::21f:29ff:fe59:f50e
C1002582.eth3 C1002582.eth3 UP UP -- 0x000000010D
IPv4: 192.168.36.231
IPv6: fe80::21f:29ff:fe59:f50c
C1002582.eth1 C1002582.eth1 UP DOWN -- 0x000000010E
IPv6: fe80::21e:bff:febe:e7c
C1002582.eth4 C1002582.eth4 UP DOWN -- 0x000000010F
IPv4: 192.168.36.233
IPv6: fe80::21f:29ff:fe59:f50f

## Slide 56: Verify Network: Failover
  The Home column lists all interfaces within the provider
  The Failover column shows the configured failover interface
  The Current column shows which interface currently owns the resources (of the interface under Home column)
  The example below shows the output when there are no failures in network
<SCF> status provider $zzcip.ztc0, detail
...
Interfaces Failover Configuration and Status:
F Home Sts LkP Failover/(Assoc) Sts LkP Current Fovr
C1002581.eth5 UP UP C1002582.eth5 UP UP C1002582.eth5 BkFO
X C1002581.bond0 -- -- -- -- C1002581.bond0 Home
...
C1002582.eth5 UP UP C1002581.eth5 UP UP C1002582.eth5 Home
C1002582.eth3 UP UP -- -- C1002582.eth3 --
C1002582.eth1 UP DOWN -- -- C1002582.eth1 --
C1002582.eth4 UP DOWN -- -- C1002582.eth4 --

## Slide 57: Verify Network: Accessibility
Ping all the configured IP addresses
<TACL> ping 10.1.100.11

## Slide 58: Verify Application: Telserv
Telnet to each of the configured IP addresses

## Slide 59: Failover: Initial Configuration
Notes: Note: Do not to forget to do a CLIMBKUP for all CLIMs when they are correctly configured.

## Slide 60: Failover: N1002582.Bond0 Switched

## Slide 61: Further sample CLIM Commands
  clim, psclim
  climconfig, climstatus
  ifstart, ifstop
  ifconfig, mii-tool, ethtool
  netstat, tcpdump
  man
Notes: <footer>
<header>
<date/time>
Check if all these work thru climcmd.

## Slide 62: (Hidden slide/full notes page)
Use this slide if needed for a:
  Full page of notes (no slide image)
  Blank page for two-sided printing of a PowerPoint student guide
Delete these instructions
Notes: <footer>
<header>
<date/time>

## Slide 63
Notes: <footer>
<header>
<date/time>