## Slide 1: IP CLIM Troubleshooting
Module 10

## Slide 2: Objectives
  Describe how to Identify a Failure
  Describe how to Categorize the Failure
  Describe how to Collect the Data
  Describe Basic Analysis
  Describe Recovery
Notes:   Do this almost in that order. If you are not sure that the problem is a duplicate, make sure that the data is collected before attempting to fix it.

## Slide 3: Identify the Failure
Various Ways to Notice a Failure
  CPU Halted
  Lost LAN Connection
  Application Failed
  OSM Alarm
  EMS Event
Notes:   Some of these might not be real failures, for example the EMS events. For suspicious looking events, check the status to confirm that there is some noticeable functionality failure.

## Slide 4: Categorize the Failure
Generic Buckets
  HOST
  CLIM
  Management
  Data (Socket)
  No-Outage (Event)
Notes:   Not easy to categorize.
  If not sure, collect data for all.
  There are some overlapping areas here.

## Slide 5: Host Failure
CPU Halt
  CPU Dump and CIP Object Files
  Event Logs ($0 and $Zlog)

## Slide 6: CLIM Failure
  CLIM Object NOT in Started State
  Event Indicating CLIM Failed
    CLIM Debuginfo
    CLIM Status

## Slide 7: Management Failure
  PROVIDER/CLIM State is NOT Started
  Missing CPU in PROVIDER Access List
    Online CPU Dumps and CIP Object Files
    EMS Logs ($0 and $Zlog)
    Status and Info of Failing CIP Objects
    CIP Trace of Monitor Process (optional)
    CLIM Debuginfo
    CLIM Status
Notes:   Online dump of the CPU logging the event (if clim is not starting)
  Fabric status in CLIM status, detail; pick the cpu/mon that is connected. (Another symptom of the failure –no access to all cpus)

## Slide 8: Socket Failure
  Application Failure
  Network Connection Failure
    Online CPU Dumps and CIP Object Files
    EMS Logs ($0 and $Zlog)
    Status and Info of Failing CIP Objects
    CIP Trace of the Provider (optional)
    CLIM Debuginfo
    CLIM Status
    CLIM Network Info

## Slide 9: No-outage Failure
  Suspicious Event
  Ambiguous Error Text
  Incorrect Help Text
    The Erroneous Text

## Slide 10: Debug Data: Host
  CPU Dump, EMS Logs
    conflist
    cipman, cipmon, cipsam
    initdll, zcipdll, zcipmdll
  SCF status, detail (all/Failing CIP objects)
  SCF info, detail (all/Failing CIP objects)
  SCF listopens, detail (MON and PROV)
  CIP MON/PROV Traces (optional)

## Slide 11: Debug Data: CLIM (1 of 2)
  CLIM Debuginfo
    Dumped At Start (After a Failure)
    Coredumps, Logs, Config Files, ..
    Zipped at /home/debuginfo Directory
    Backup (or sftp) to NSC/NonStop server
    Move/Delete the Old Files
  Climcmd could be used to collect Data

## Slide 12: Debug Data: CLIM (2 of 2)
  CLIM State
    Climcmd <clim> climstatus
  CLIM Network Info
    Multiple commands (use obey file)
    Climconfig
    Other Tools (ip, netstat, route, ifconfig, ..)

## Slide 13: Basic Analysis
  Additional procedures in the future (FCS)
    Check CIP Software Version
    Check the Status of CIP Subsystem
    Check CLIM Software Version
    Check the CLIM Status
  Procedures Detailed in later slides

## Slide 14: Basic Analysis: CIP
  CIP Status (SCF)
    status mon $zzcip.* (Started State)
    status clim $zzcip.* (Started State)
    status prov $zzcip.* (Started State, for both Status and TPStatus fields)

## Slide 15: Basic Analysis: CLIM
  CLIM Status (CLIMCMD)
    climstatus –os (current ServerNet status)
    climstatus –oc (shows climprep values)
    cat /proc/bsky/interface [0|1] (NC check)
    psclim (shows clim process status)
Notes:   If the CLIM is not in started state, these are a few things to try to check if the connections and climprep are correct.
  DL385FA:17:13:49:~# climstatus –os CLIM Configuration & Status:
  Mode..................... IP
  State.................... STARTED
  ConnPts.................. 2
  X1 Location.............. Group 100, Module 2, Slot 3, Port 1, Fiber 0
  Y1 Location.............. Group 100, Module 3, Slot 3, Port 1, Fiber 0
  X2 Location.............. Group 100, Module 2, Slot 3, Port 2, Fiber 0
  Y2 Location.............. Group 100, Module 3, Slot 3, Port 2, Fiber 0
  X1 Connection Status..... UP
  Y1 Connection Status..... UP
  X2 Connection Status..... UP
  Y2 Connection Status..... UP
  Last Restart Time........ Thu Jan 31 17:11:44 2008
  CIP/Linux Hostname....... DL385FA
  Network SW Version....... T0691H01_01MAY2008_AAA_CLIM
  Storage SW Version.......
  CIP SW Version...........
  Number of Socket Servers. 1
  CIP/Linux Version:
  Linux version 2.6.18-5-telco-amd64 (Debian 2.6.18.dfsg.1-15hpde1.4haleytest2) (dannf@hp.com) (gcc version 4.1.2 20061115 (prerelease) (Debian 4.1.1-21)) #1 SMP PREEMPT Wed Jan 16 00:39:09 UTC 2008

## Slide 16: Trace Commands
  Trace CIPMON
    scf trace ..
  Trace PROVIDER
    scf trace ..

## Slide 17: Recovery: NonStop Server
Stop/Start CIP
  stop failing object
  stop proc $zzcip, sub all
  stop proc $<sam>
  diver/reload cpus
  coldload system

## Slide 18: Recovery: CLIM
  Built-in CLIM Recovery Mechanism
    Restarts the CLIM CIP Software if a module fails
    Reboots the CLIM (Restart Threshold Exceeded)
    Disables CIP software (Reboot Threshold)
    Requires operator intervention to start
    Reset Failure Threshold
    Save CLIM Debuginfo
    Reboot CLIM
  If the CLIM did not detect Failure
    Restart the CLIM Software
      Abort the CLIM
      Save CLIM Debuginfo
      Start the CLIM Software
    Reboot the CLIM

## Slide 19: Status MON $ZZCIP.* Status MON $ZZCIP.ZCM02,DETAIL
Notes:   Fabric Status displays the connections to each known CLIM and the availability of the X and Y ServerNet fabrics. The Mgmt column shows the management connection to CLIMAGT, the Data column shows the data path connections to the CIPSSRV processes, and the Numdata column shows the number of CIPSSRV processes.
  The status is shown as follows:
  – No connection is established.
  – X Connection is established, only the X fabric is available.
  – Y Connection is established, only the Y fabric is available.
  – XY Connection is established, both X and Y fabrics are available.

## Slide 20: Status Provider $ZZCIP.*
Notes: -> STATUS PROVIDER $ZZCIP.*
CIP Status PROVIDER \MYSYS.$ZZCIP.*
Name Status CLIM Trace
ZTC0 STARTED CLIM1 OFF
ZTC1 STARTED CLIM2 0, 1
ZTC2 STARTED CLIM3 OFF
Trace
shows a list of the processors that have started
a trace on the Provider, or OFF if none.
-> STATUS PROVIDER $ZZCIP.ZTC1, DETAIL
CIP Detailed Status PROVIDER \MYSYS.$ZZCIP.ZTC1
State.................... STARTED
CLIM..................... CLIM2
Current Access........... ( 0, 1, 2, 3, 5, 7 )
Trace Status:
CPU Filename
0 \MYSYS.$DATA00.TRZTC1.CPU0
1 \MYSYS.$DATA00.TRZTC1.CPU1
Current Access
shows the processors that have established access
to the Provider.
Trace Status
shows the processors that are tracing the Provider
and each trace file name.

## Slide 21: Status CLIM $ZZCIP.*

## Slide 22: Status CLIM $ZZCIP.DL385FA,DETAIL
Notes: 4-> help cip status clim
  The STATUS CLIM command displays the current status of the specified CLIM object(s) on the target system. The summary display shows the summary state, which reflects the last START/STOP/ABORT command issued to the object.
  The detailed display also shows the status of the CLIM interfaces and the connections to the CLIM from the individual CIPMONs. Similar information from the CLIM viewpoint can be displayed using the CIP/Linux climstatus command on the CLIM.
  The syntax for the STATUS CLIM command is:
  STATUS [/OUT <file-spec>/] CLIM <clim-name> [ , DETAIL ] <clim-name> is the name of the CLIM to display. A wildcard can specify a set of CLIMs.
  Considerations
  None.

## Slide 23: Listdev TCPIP

## Slide 24: Listopens MON $ZZCIP.ZCM00

## Slide 25: Listopens Provider $ZZCIP.MPRO1

## Slide 26: CIP: How To Determine Eth0 IP Address
SCF Status CLIM $ZZCIP.DL385FA, DETAIL

## Slide 27: CIP: How To Determine Eth0:0 IP Address
SCF Status CLIM $ZZCIP.DL385FA, DETAIL

## Slide 28: CIP: How To Determine Maintenance Provider IP Address
SCF Status PROVIDER $ZZCIP.ZTCP0, DETAIL

## Slide 29: CIP: How To Display Versions

## Slide 30: EMS Events

## Slide 31: EMS Event Detail

## Slide 32: CLIM Commands (1 of 4)
Check Status of CLIM CIP Software
  climcmd <clim> psclim
Notes:   You should see at least those 4 processes.

## Slide 33: CLIM Commands (2 of 4)
  Abort a CLIM
    climcmd <clim> clim abort
  Dump the Debugdata
    climcmd <clim> clim debuginfo

## Slide 34: CLIM Commands (3 of 4)
  Start a CLIM
    climcmd <clim> clim start

## Slide 35: CLIM Commands (4 of 4)
  Reset Failure Threshold
    climcmd <clim> clim clearlog
  Reboot CLIM
    climcmd <clim> clim reboot
    Use break-key to get Prompt
  Get CLIM Specific Status
    climcmd <clim> climstatus

## Slide 36: CLIM Status Commands (1 of 2)
Get Climprep Attributes

## Slide 37: CLIM Status Commands (2 of 2)
Get Servernet Status

## Slide 38: ServerNet Neighbor Check Status

## Slide 39: Debugdata Commands
  Check the Latest Debugdata
    climcmd <clim> ls –lrt /home/debuginfo
  Retrieve the Debugdata
    use sftp from Tacl (in binary mode)
  List the Contents in Debugdata
    climcmd <clim> tar –tvf /home/debuginfo/<file>

## Slide 40: Displaying the Latest Debugdata

## Slide 41: Displaying the Debugdata Contents

## Slide 42: Commands To Gather CLIM Network Information
  climcmd <clim> climconfig arp –info
  climcmd <clim> climconfig interface –info all
  climcmd <clim> climconfig route –info
  climcmd <clim> climconfig route –info –usrconfig
  climcmd <clim> climconfig snmp –info
  climcmd <clim> climconfig sysctl –info all
Notes: CLIM Config info:
climconfig arp –info
climconfig hostname –info
climconfig interface –info all
climconfig route –info
climconfig route –info –usrconfig
climconfig snmp –info
climconfig bondmode –info
climconfig sysctl –info all
climconfig tunnel –info all

## Slide 43: Commands to Gather Network Related Information
  climcmd <clim> ifconfig –a
  climcmd <clim> ip –v4 addr show
  climcmd <clim> ip –v6 addr show
  climcmd <clim> ethtool eth<n>
  climcmd <clim> netstat –pane
  climcmd <clim> route
  climcmd <clim> slnpconfig -l
Notes: CLIM Network Info -- Use these via climcmd
arp –n - ARP cache table information
ifconfig -a - Interface settings
ip -4 addr show - the ip tool is for checking or setting IP configuration
ip -6 addr show settings
ip link show
ip maddr show
ip neigh show
ip route show
ip rule show
ip tunnel show
ethtool eth<n> - checking up or setting Ethernet configuration settings, like duplex and speed
netstat -pane - list the current states of all sockets including openers
route - looking up routing information
slnpconfig -l - Add/Delete/List Simple Logical Network Partition (SLNP) Rules
sysctl -A - looking up kernel parameters - including network settings

## Slide 44: CLIMCMD Netstat

## Slide 45: TCPDUMP trace utility
  tcpdump is the utility to trace Ethernet and IP traffic on a CLIM
  Output can be send to the screen in readable format or to a file in binary format
  The binary format can be read by utilities like Wireshark.(new name for Ethereal) Look at www.wireshark.org for free download.
    Syntax: tcpdump [-aAdDeflLnNOpqRStuUvxX] [-c count] [ -C file_size ]
    [ -E algo:secret ] [ -F file ] [ -i interface ] [ -M secret ]
    [ -r file ] [ -s snaplen ] [ -T type ] [ -w file ]
    [ -W filecount ] [ -y datalinktype ] [ -Z user ]
    [ expression ]
Notes: To start trace use: climcmd <clim_name> tcpdump host <destination_ip -i eth<n> -w /home/trace_file -v To stop the trace: - Break the session where you started the trace. - climcmd clim_name ps| grep tcpdump look for tcpdump; check pid - climcmd clim_name kill -2 <pid> (tcpdump process might already be stopped) - climcmd clim_name ls -lrt /home (check the trace file is there) - sftp -S $ssh_process -h root@clim_ip_address:/home/trace_file (transfer to nonstop) - climcmd clim_name rm /home/trace_file (remove file from clim)
Analyze it with a utility like wireshark

## Slide 46: TCPDUMP analysis
Notes: As you can see Wireshark is a GUI with simple tools to select frames and packets based on MAC addresses, IP addresses, protocols and much more.

## Slide 47: Display the Link Status of an Ethernet Port

## Slide 48: Other CLIM Network Commands
  Locate an Ethernet Port
    climcmd <clim> ethtool –p eth<x> <sec>
    makes the ‘red’ LED on the eth<x> port blink for <sec> seconds.
  Scan CLIM syslog real time
    climcmd <clim> tail –f /var/log/syslog

## Slide 49: Retrieve IP and Mac Address for eth0

## Slide 50: Display Time Zone

## Slide 51: Add or Retrieve Trap Sink Information

## Slide 52: Other Useful CLIMCMD Commands
  Find out the version of CIP software
  Displaying uptime since the last reboot of the CLIM

## Slide 53: Displaying the Disk Space Usage